Charisma 1 & 2 & FS Property Management

Level 1 Energy Audit

9000 Jane St,

Vaughan, ON L4K 0M6

Feb-26-2026

Prepared by:

Mann Engineering

1110 FINCH AVENUE W, SUITE 706

TORONTO, ON M3J 2T2

Web: Mann Engineering

Phone: 416 201 9109

Table of Contents

1. Executive Summary	4

1.1	Description of this Study 	4

1.2	Recommendations for Improvement 	4

2. Facility and Systems Description	5

2.1	General Facility Overview	5

2.2	Building Mechanical Systems Overview	5

2.2.1 Central Heating/Cooling Systems	5

2.2.2 Central Ventilation System	6

2.2.3 DHW System	7

2.2.4 Miscellaneous	7

3. Energy Conservation Measures	9

Appendix A – ASHRAE Level II Energy Audit Proposal	10

List of Abbreviations

Btu	British Thermal Units

CFL	Compact Fluorescent Lamp

Cfm	Cubic Feet per Minute

CO2	Carbon Dioxide

DHW	Domestic Hot Water

ekWh	Equivalent Kilo Watt Hours

° F	Degree Fahrenheit

Fc	Foot-candle

GJ 	Giga Joules, Unit for Measuring Heat Content

HP	Horse Power

HWS	Hot Water Supply

HVAC	Heating, Ventilation, and Air Conditioning

ID	Equipment Identification Tag

BAS	Building Automation System

LB	Pound

LED	Light Emitting Diode

kW	Kilo Watt, a Measure of Electric Demand

kWh	Kilo Watt hours, a Measure of Electricity Usage

m3	Cubic Meter

Max	Maximum

MBH	1,000 Btu per hour

MH	Metal Halide Min Minimum

MMBtu / hr	Million Btu per hour

NA	Not Available or not applicable

NRCAN	Natural Resources Canada

OAT	Outside Air Temperature

O & M	Operations and Maintenance

DDC	Direct Digital Controls

VFD	Variable Frequency Drive

VAV	Variable Air Volume

# Executive Summary

## Description of this Study

Mann Engineering performed an ASHRAE Level 1 Energy Audit at 9000 Jane St, Concord, in Vaughan, Ontario. The structure is a 29 & 28 floor-storey condominium comprising 345 & 306 units residential units constructed in 2023.

Mann reviewed the existing HVAC system from visual inspection and discussions with co-operative on-site staff, we attained un understanding of operation characteristics of the facility. This preliminary audit does not include full utility consumption analysis, financial modelling or detailed energy-saving quantification.

To support capital planning with verified energy-saving calculations, project budgeting, incentive alignment, and payback estimation, it is recommended that the client advance to a Level II audit (detailed building energy and financial assessment) to evaluate energy conservation and project financial viability. Additional retrofit measures are likely to emerge once the analysis extends to this audit depth.

## Recommendations for Improvement

Based on the results from the above analysis and our site observations, a series of building improvement measures were formulated. This report summarizes the existing conditions observed during the site visit, identifies major opportunities for energy savings and operational improvements, and provides preliminary recommendations. Photographs taken during the walkthrough are included to illustrate key equipment and findings.

| Number | Description of Measure | Estimated Utility / Cost Savings |
| --- | --- | --- |
| 1 | Install New Building Automation System (BAS) | Install a new central BAS to Control boilers, DHW, MUAs, pumps and exhaust fans with scheduling, reset and remote access, reducing energy use and maintenance. Improve building operation and management. |
| 2 | Boiler Plant Optimization & Hydronic Balancing | Optimize the existing boiler plant through hydronic and control improvements to restore condensing performance without replacing major equipment. Qualified for Enbridge incentives. |
| 3 | Primary–Secondary Boiler and Hydronic Loop Reconfiguration (Primary loop + WSHP loop + DHW loop) | Reconfigure Primary heating loop, WSHP loop and DHW loop to a primary–secondary layout, hydraulically separating loops to improve temperature control, boiler protection and plant efficiency. |
| 4 | Replace Pool AHU and Exhaust Fan with Dry-O-Tron Unit | Replace the pool AHU and exhaust fan with a Dry-O-Tron-type dehumidification unit that recovers heat while tightly controlling pool humidity and temperature. |
| 5 | EV Charging Stations | Plan and install EV charging infrastructure for residents and staff, contact us for more detail. |

# Facility and Systems Description

## General Facility Overview

A walk-through Level 1 energy audit was performed at 9000 Jane St, Concord, in Vaughan, Ontario. a 29 & 28 floor-storey condominium constructed in 2023. The architectural condition of the building is good. It has a mixture of 3 Bedroom, 2 Bedroom, 1 Bedroom. suites for a total of 345 & 306 units units. The site visit included a comprehensive walk through, review of all mechanical rooms and equipment and an interview with the building operator.

## Building Mechanical Systems Overview

### Central Heating/Cooling Systems

Existing conditions:

One high temp loop boiler plant:.

The building is served by a high temperature loop and is generated in the central mechanical room.

The boiler plant is located in {location} consist of (number of HTG boiler)gas-fired boiler. These are separated into:

High temperature loop boiler:

{number of boiler} {atmospheric/non-condensing/condensing}  boilers rated at {HTG boiler capacity} MBH each,efficiency xx %.Manufactured in {year of manufactured} which serve building's primary hot water loop. Hot water generated by the boilers is distributed to {in-suite fan coil units/ in-suite radiator} and also serves additional hydronic loads, including radiation, and heat exchanger circuits. Supply temperature at {supply temp} with return temperature at {return temp}

Miscellaneous Load Boiler:

{number of boiler} {atmospheric/non-condensing/condensing} boilers rated at {boiler capacity} MBH each, with a nominal thermal efficiency of {efficiency %}. Manufactured in {year of manufacture}, these boilers serve miscellaneous hydronic loads within the building, including {misc loads – e.g., snow-melt system, pool heating, garage heating coil, reheat coils, perimeter radiation, heat exchanger circuits}. Hot water generated by the boilers is distributed through dedicated piping loops serving the identified auxiliary loads. The system operates at a supply temperature of approximately {supply temp}°F with a return temperature of {return temp}°F under design conditions.

Good condition + Working normally:

The boilers were observed to be in good condition, with no visible leakage or abnormal noise noted around the boiler plant at the time of the site visit. Distribution pumps and associated hydronic piping were observed to be operating normally, and no circulation issues were reported by on-site staff during the walkthrough

The heating plant includes a relatively high number of boilers, which increases maintenance complexity, spare parts requirements, and overall lifecycle costs. This configuration can also complicate system sequencing and balancing, particularly under part-load conditions.

While the existing boilers are high-efficiency condensing units; however, they are currently operating without effective condensing due to elevated return-water temperatures, at {154F}. Condensing boilers only achieve high efficiency 90+% at return water temperatures below 130F. This operating condition limits achievable efficiency gains and restricts the ability to operate the heating system at lower supply and return water temperatures. As a result, opportunities for system optimization are constrained, and compatibility with low-temperature, high-efficiency heating strategies is reduced.

The boilers are operating at or near design supply temperatures, resulting in elevated supply and return water temperatures. This operating condition may indicate limited outdoor air temperature reset and/or a lack of effective modulating control. Operating at consistently high water temperatures reduces opportunities for control optimization, increases distribution and standby heat losses, and limits potential energy savings, particularly during part-load and shoulder-season conditions.

A centralized Building Automation System (BAS) is not present for the heating boiler plant. The system relies on multiple standalone control panels and local sensors, which limits coordinated control and system-level visibility. Additional integration through a BAS would improve equipment scheduling, system monitoring, fault detection, and overall heating system energy performance.

Existing conditions:

Fancoil + chiller:

Cooling is provided by a central York water-cooled chiller located in the main mechanical room. The chiller was manufactured in {2002 and is original to the building}.

Heat rejection is provided via a {B.A.C}. cooling tower installed in {2004}. The condenser water system, including the cooling tower fan and condenser water pumps, are {not equipped with VFDs}.

The chilled-water distribution system appears to be {functioning normally}, with supply and return piping, pumps, and control valves observed to be in serviceable condition at the time of the walkthrough. According to site staff, the chiller operates {reliably} under typical summer conditions.

Suite-level cooling is provided by in-suite fan coil units operating under local thermostatic control. These fan coils distribute chilled water from the central plant to provide space cooling throughout the suites. {Where fan coil units are original to the building, they may be approaching the end of their typical service life and could require future replacement.}

At the time of the site visit, the chiller and cooling tower were {seasonally shut down}, which is typical for the time of year. No major physical deficiencies were identified during the walkthrough, and building staff reported generally reliable operation during the most recent cooling season.

Over all Good condition - With BAS Integration:

Cooling system operation is integrated into the Building Automation System (BAS), allowing centralized monitoring and coordination of plant equipment.

At the time of the site visit, the Cooling System appeared to be functioning normally, with no major deficiencies observed. The BAS provides a foundation for coordinated operation and improved scheduling.

Minor refinement of scheduling and temperature reset strategies may provide incremental efficiency improvements over time

A centralized Building Automation System (BAS) is not present for the cooling system. Integrating the chiller plant into a BAS would enable proper equipment sequencing, temperature and pressure reset control, and demand-based operation, resulting in significant improvements in system efficiency and overall performance.

### Central Ventilation System

Existing condition:

Rooftop MUA:

Ventilation for the building is provided by One (1)make-up air (MUA) units, located in roof top, serving corridors and other public areas.

1 central MUA w\ VFD + 2 MUA w VFD + Plate and frame heat exchangers:

The building is equipped with one (1) central MUA unit located in the penthouse serving most residential floors, and three (3) fresh-air MUA units located in the ground-floor mechanical room serving common areas.

The penthouse central MUA is equipped with a VFD, during the site visit it was observed operating at approximately 48 Hz (80%). The ground-floor MUA units include two units with VFDs;

No occupancy-based scheduling or demand control was observed, three (3) fresh-air MUA units appear to operate at or near constant speed regardless of actual ventilation demand.

All units are equipped with heating and cooling coils served by glycol loops connected to the primary heating and cooling systems through shell-and-tube heat exchangers. These heat exchangers are difficult to service, limiting maintainability and increasing long-term operational risk.

The MUA systems were observed to be functionalwere originally installed circa 2004. Based on typical service life expectations for commercial ventilation equipment, the units are approaching the end of service life. While no immediate deficiencies were identified, the current configuration presents opportunities for improved control, energy efficiency, and future lifecycle upgrades.

Plate and frame heat exchanger:

All units are equipped with heating and cooling coils served by glycol loops connected to the primary heating and cooling systems through plate and frame heat exchanger. These heat exchangers are in general good conditions.

AHU units with VFD capacity, but not integrate into BAS:

Although the AHU units are in generally good mechanical condition, the building is not equipped with a centralized Building Automation System (BAS) to coordinate AHU operation with the rest of the mechanical systems.

Integration of the existing VFD-controlled AHU units into a BAS would enable improved scheduling, supply air temperature reset, demand-based ventilation, and alarm monitoring. These enhancements would improve overall energy performance, operational oversight, and long-term system reliability.

Hydronic MUA + good conditions:

Supply-air temperatures and airflow patterns were generally consistent with normal operation. Hydronic heating coils are served from the building’s high-temperature heating loop. Overall, the MUA systems appear to be functioning as intended, with minor operational and control improvements possible to enhance performance and consistency.

Although the MUA units are in generally fair mechanical condition, the building is not equipped with a centralized Building Automation System (BAS).

Integration of the existing VFD-controlled MUA units into a BAS would enable improved scheduling, supply air temperature reset, demand-based ventilation, and alarm monitoring.

### DHW System

Existing condition:

Central DHW boilers plant:

Domestic hot water is generated in the central mechanical room, located in PentHouse by (number of DHW boiler)gas-fired boiler.

Atmospheric DHW Boiler:

(Number) atmospheric DHW boilers, each rated at approximately (Capacity) MBH, install in around (Year). Supply temperature was approximately {supply_temp}°F with return at {return_temp}°F.

Indirect storage tank:

Two (2) indirect storage tank was observed, located at the main boiler room and is heated via DHW boiler. The tank was observed to be in good mechanical condition.

Mechanical Mixing valves:

Thermostatic mixing valves set to approximately 120°F were observed and appeared to be in good mechanical condition.

DHW balancing issue+ Future optimization BAS:

Domestic hot water complaints were reported in the West Tower during peak demand periods (approximately 8:00 AM and 6:00 PM), particularly in the mid and upper zones. Lower zone performance was reported to be stable during these periods.

Site review confirmed that DHW boiler capacity is adequate and that storage tank and mixing valve setpoints are operating within normal ranges. Based on these observations, the issue is not related to insufficient boiler capacity or control setpoints.

The temperature drop during peak demand may be associated with storage tank sizing relative to peak draw, zoning distribution imbalance, or recirculation performance in upper zones

Further review of storage volume, recirculation flow rates, and zoning configuration is recommended to confirm root cause.

### Miscellaneous

Existing condition:

Lighting condition and controls:

Lighting throughout the building is generally in good working order. Common areas, corridors, and mechanical rooms appear to be fully equipped with LED. No widespread outages were observed during the walkthrough, and the overall lighting levels were appropriate for the building’s use. Further savings may be available through the use of occupancy-based controls in selected low-traffic areas. Or installing light control in the parking area.

Envelope Condition (Good):

The building envelope appears to be in generally good condition, with no significant signs of air leakage or deterioration observed at the time of the site visit. Envelope components appear to be performing as intended.

Window condition (good):

The building is equipped with double-pane windows with generally intact seals and caulking, providing effective air sealing and thermal performance. No significant air infiltration issues were observed during the site visit

Garage ventilation (Has CO controls):

The parking garage is served by a mechanical ventilation system controlled by carbon monoxide (CO) sensors. Exhaust fans start and stop in response to measured CO levels, providing demand-based operation and reducing unnecessary runtime during periods of low vehicle activity. The garage fans and control system appeared to be functioning normally, with no obvious mechanical deficiencies reported.

Unheated garage:

The building includes an unheated parking garage, which is typical for buildings of this age. No dedicated space-heating system was observed, and garage temperatures are allowed to fluctuate with outdoor conditions.

Has VFD on Booster Pump:

The building is served by a packaged domestic water booster pump system equipped with variable frequency drives (VFDs). The booster pack modulates pump speed in response to system demand, maintaining stable water pressure throughout the building while reducing unnecessary energy consumption during low-demand periods. The booster pump system was observed to be operating normally at the time of the site visit, with no abnormal noise, vibration, or visible mechanical deficiencies noted

Electric ramp heating:

The exterior ramp heating system is hydronic ramp heating and is used to maintain safe, ice-free conditions during winter months. No operational issues were observed with the ramp heating system at the time of the visit. Control improvements may be possible by converting the electric ramp heating system to a hydronic system, where feasible, to reduce electrical energy consumption while maintaining winter safety performance

Natural Gas Generator:

The building is equipped with a natural gas emergency generator to provide backup power to designated life-safety and essential systems during utility outages. The generator is connected to the building’s natural gas supply, eliminating the need for on-site fuel storage. Regular inspection, operational testing, and preventive maintenance are required to ensure system reliability and compliance with applicable electrical and fire safety regulations.

No Dectron unit for swimming pool:

The indoor pool area is served by a hydronic MUA located in M floor, providing ventilation, dehumidification, and space conditioning. The unit is designed to control humidity levels, maintain indoor air quality, and prevent condensation-related deterioration within the pool enclosure

# Energy Conservation Measures

## Measure 1 – Install New Building Automation System (BAS)

Existing Conditions:

The existing HVAC mechanical systems—including MUAs, exhaust fans, heating boilers, DHW plant, cooling equipment, and pumps—are controlled manually or via basic local thermostats and temperature sensors. There is minimal outdoor-air reset, limited boiler sequencing, and no centralized scheduling or monitoring. Equipment often operates during unoccupied periods, leading to excessive energy use and chronic overheating.

Retrofit Conditions:

It is recommended to install a centralized BAS to control all major HVAC systems. The BAS would provide occupancy-based scheduling, outdoor-temperature reset for boilers, zone-level temperature modulation, real-time monitoring, remote access, and alarm notifications. Improved control will reduce unnecessary run time, lower energy consumption, and improve comfort while reducing maintenance costs through better diagnostics. Utility incentives for advanced building controls can further improve project economics, with typical paybacks on the order of 3–4 years.

*Where applicable, IESO incentives and Enbridge incentives for central heating system efficiency upgrades may be available and could help improve overall project economics. Additional information regarding current incentive programs can be found on Mann Engineering’s website:

https://www.mannengineering.com/100-000-enbridge-incentive

Key Inputs:

Category: BAS / Controls

## Measure 2 – Boiler Plant Optimization & Hydronic Balancing

Existing Conditions:

The central heating plant consists of eight (8) condensing boilers installed circa 2014. Although the boilers are designed for high-efficiency condensing operation, the system is currently operated with elevated supply-water temperatures, with observed setpoints typically in the range of approximately 140°F to 150°F. Based on operator feedback, these aggressive setpoints are maintained to satisfy the heating demands of the Make-Up Air (MUA) units, which share the primary heating loop, and to compensate for localized flow restrictions within the distribution piping.

Under these operating conditions, return-water temperatures are likely elevated for much of the heating season, limiting the boilers’ ability to operate in condensing mode and effectively reducing efficiency to non-condensing levels. The existing hydronic configuration does not provide sufficient separation between the higher-temperature MUAloads and the lower-temperature building heating loop, restricting the ability to reset supply temperatures independently.

Retrofit Conditions:

Mann recommends pursuing boiler plant optimization through the Enbridge Gas Boiler Optimization Pilot Program. This program supports optimization of existing boiler plants through a phased approach rather than equipment replacement. The initial phase includes a detailed engineering assessment, funded by the program, to evaluate system flow characteristics, control limitations, and hydronic configuration.

Based on the assessment findings, the retrofit scope may include hydronic separation between the MUA and building heating loops, corrective system balancing to address flow restrictions, and optimization of BAS control strategies. These measures would allow the boiler outdoor-air reset curve to be lowered while maintaining adequate MUA heating, enabling return-water temperatures to drop into the condensing range.

This approach restores the boiler plant closer to its intended design performance, increases seasonal efficiency, and maximizes the value of the existing assets without the capital cost of boiler replacement.

Key Inputs:

Category: Boiler / Plant

## Measure 3 – Primary–Secondary Boiler and Hydronic Loop Reconfiguration (Primary loop + WSHP loop + DHW loop)

Existing Conditions:

The existing piping arrangement separates the WSHP loop, primary heating loop, and domestic hot water (DHW) loop into independent hydronic systems, each served by dedicated boilers and pumping configurations. The primary heating loop operates at higher temperatures for space heating, the WSHP loop operates at lower temperatures, and the DHW system functions on a separate loop without hydraulic or control integration. This configuration increases system complexity and limits opportunities for load diversity, heat recovery, and coordinated temperature optimization. During shoulder seasons, independent loop operation can contribute to boiler short cycling, elevated supply temperatures, and reduced overall plant efficiency.

Retrofit Conditions:

It is recommended to evaluate reconfiguring the WSHP loop, primary heating loop, and DHW piping into a coordinated Primary–Secondary (P-S) hydronic arrangement. Under a P-S configuration, a central boiler primary loop would maintain controlled supply temperatures while secondary loops draw only the required flow and temperature for each load. This arrangement provides hydraulic separation, allows differentiated temperature control for high- and low-temperature systems, improves outdoor-air reset effectiveness, and reduces short cycling. Improved integration may also enhance return-water temperature control, supporting more efficient boiler operation. When implemented in conjunction with condensing boiler upgrades, this redesign may allow optimization of boiler staging and potential reduction in total boiler count, thereby lowering long-term maintenance complexity and operating costs. Further engineering review is required to confirm detailed hydraulic configuration, load diversity assumptions, and control sequencing strategy.

*Where applicable, IESO incentives and Enbridge incentives for central heating system efficiency upgrades may be available and could help improve overall project economics.

Additional information regarding current incentive programs can be found on Mann Engineering’s website:

https://www.mannengineering.com/100-000-enbridge-incentive

Key Inputs:

Category: Hydronic Loops

## Measure 4 – Replace Pool AHU and Exhaust Fan with Dry-O-Tron Unit

Existing Conditions:

The swimming pool area is currently served by a conventional air-handling unit and separate exhaust fan. Humidity control is limited, and there is no integrated heat recovery between exhaust and supply air. This can lead to higher space heating loads, condensation issues and comfort complaints in the pool area.

Retrofit Conditions:

It is recommended to replace the existing pool AHU and exhaust fan with a packaged dehumidification unit such as a Dry-O-Tron. This type of system combines dehumidification, space heating and exhaust heat recovery in a single unit, controlling humidity and pool water temperature to defined setpoints. Recovered heat can be used to warm supply air or pool water, reducing overall energy consumption. Detailed engineering is required to size the unit and confirm ductwork and structural requirements.

Key Inputs:

Category: Other / Misc

## Measure 5 – EV Charging Stations

Existing Conditions:

Electric vehicle (EV) ownership is expected to grow substantially over the next decade, and many multi-residential and commercial buildings currently lack dedicated EV charging infrastructure for residents, staff, or visitors

Retrofit Conditions:

Upgrading through the Trade‑In Program is recommended to replace outdated units with OCPP‑networked TAR‑M chargers, providing managed access, usage metering, and load balancing. Early participants benefit from reduced capital cost, including no‑cost upgrades for the first two owners, along with ongoing carbon‑credit rebates of $0.03–$0.05/kWh.

*Additional information regarding current incentive programs can be found on Mann Engineering’s website:

https://www.mannengineering.com/

Key Inputs:

Category: Other / Misc

Appendix A – ASHRAE Level II Energy Audit Proposal

Next step:

As the recommended next step following this ASHRAE Level I Energy Audit, Mann Engineering proposes completing a comprehensive ASHRAE Level II Energy Audit Report. This enhanced study provides a deeper technical analysis of the building’s mechanical and electrical systems and develops project-specific cost, savings, and payback models to support informed capital planning. Please refer to the proposal on the following page for our detailed quotation.

The ASHRAE Level II Audit includes:

- Detailed analysis of utility bills and consumption trends

- Engineering-based cost estimates for recommended measures

- Modelled energy-saving calculations for each opportunity

- Available incentives estimate from Enbridge and IESO Save on Energy Program.

- Financial modelling, including payback periods and cash flow analysis

By combining technical evaluation with financial forecasting, the Level II Audit helps the client make more informed, evidence-based decisions regarding future capital projects and investment prioritization.

.

Attention:	Charisma 1 & 2 & FS Property Management (“Client”)

From:	Wesley Mann, (wmann@mannengineering.com)

Date:	Feb-26-2026

Subject:	ASHRAE Level II Energy Audit Proposal at 9000 Jane St

This letter is an engineering proposal (“Proposal”)

Background

Mann Engineering (“Mann”) is a professional consulting engineering company that specializes in energy management, including energy audits, engineering, project management and implementation. Our firm has hundreds of installed energy management projects, including design/build projects, and we have been in business since 1988 and we offer one-year limited warranty on all services provided.

We offer the following accreditations:

- Licensed by the Professional Engineers of Ontario (PEO)

- Optional registration with the The Association of Professional Engineers and Geoscientists of Alberta (APEGA), The Association of Professional Engineers and Geoscientists of British Columbia (APEGBC), The Association of Professional Engineers and Geoscientists of Manitoba (APEGM), The Association of Professional Engineers and Geoscientists of New Brunswick (APENB), The Association of Professional Engineers and Geoscientists of Saskatchewan (APEGS), The Associations of Engineers of Nova Scotia, The Association of Professional Engineers of Newfoundland & Labrador, conditional upon request, application and approval

- Full in-house mechanical, electrical and structural consulting engineering services

- Covered with Professional Liability Insurance with Evolution Insurance Inc.

- Registered with the Technical Safety Standards Association (TSSA)

- Fully bonded with Marsh Canada

- Member of the Toronto Better Building Partnership

- Full in-house mechanical construction capability

- Full in-house electrical construction capability

- Full in-house building automation design and implementation capability

- Full in-house 24-7 monitoring service for HVAC and energy services

Introduction

Mann Engineering (“Mann”) has been requested to provide a proposal for an ASHRAE Level II Energy Audit at 9000 Jane St. The primary goal of the Client is to verify the condition and remaining lifespan of the mechanical equipment throughout the building. In addition, the energy audit will evaluate the existing energy consumption of the facility (natural gas, electricity and water) and propose energy management measures with detailed analysis.

ASHRAE Level II Energy Audit

Scope of Work

We would like to propose the following services with the scope of work shown below:

- One detailed site review by Mann Engineering

- Review all HVAC equipment on site and provide recommendations on equipment remaining lifespan and repair/replacement options.

- Analysis of water, natural gas, and electricity bills over the past 12 months.

- Benchmarking of utilities, where applicable

- Analysis of the ventilation system in the building

- Analysis of the DHW system in the building

- Analysis of the heating/cooling systems in the building

- Analysis of water fixtures and systems in the building

- Analysis of the lighting systems in the building

- Analysis and potential benefits of a building automation system

- Analysis of the opportunities to reduce energy consumption on a measure-by-measure basis

- Analysis of the costs associated with the identified energy management measures

- Analysis of the potential savings associated with the identified energy management measures

- Analysis of the potential incentives associated with the identified energy management measures

- A proposed strategy for implementing the identified energy management measures

- A formal written report (electronic copy).

- Energy Audits will be qualified under ASHRAE Level II requirements

- Apply for and manage any available incentives.

Our Fee

Our base fee for the above Scope of Work is $12,000 plus taxes.

This price includes all miscellaneous costs such as photocopying and other disbursements.

Incentives

- Enbridge Incentive: Eligible participants under the Enbridge 2026 Program may be eligible to recover up to 50% of the audit cost (to a maximum of $6,000), subject to program terms and approval.

*Enbridge funding is limited and available on a first come first served basis. Funding will be confirmed prior to conducting the energy audit.

Terms

- 20% to be invoiced on start of project.

- Balance on submission of final report.

- Applicable taxes extra to all prices.

- All invoices are net 30 days.

- Any change to scope of work will be billed according to our Standard Billable Rates.

- Quotes valid for 30 days.

We appreciate the opportunity to provide this quote,

Your signature indicates acceptance of the terms of this agreement, including Schedule A and Schedule B, including the STANDARD TERMS AND CONDITIONS, approval to proceed with the chargeable scope of work, and that these agreements are binding on the Client. Schedule A and Schedule B form an integral part of the Mann Proposal. The Proposal containing the proposed Scope of Work, together with Schedule A and Schedule B, are collectively referred to as the "Agreement".

SIGNATURES:

Mann Engineering	Name

Signature:

I have authority to bind the corporation.

Name

CLIENT

Signature:

I have authority to bind the corporation.

PO#

SCHEDULE A: STANDARD BILLABLE RATES 2026

ENGINEERING, MECHANICAL, CONTROL, & ELECTRICAL DEPARTMENTS (Add $30 for Structural)

|  |  | Per Hour |
| --- | --- | --- |
| Principal | ………………………………………… | $600.00 |
| Manager | ………………………………………… | $195.00 |
| Senior Engineer | ………………………………………… | $180.00 |
| Intermediate Engineer | ………………………………………… | $150.00 |
| Designer/Junior Engineer | ………………………………………… | $120.00 |
| Engineering Technician | ………………………………………… | $ 120.00 |
| Field Technician | ………………………………………… | $ 120.00 |
| Senior Administration | ………………………………………… | $ 75.00 |
| Junior Administration | ………………………………………… | $ 70.00 |
| Senior Accountant | ………………………………………… | $ 75.00 |
| Junior Accountant | ………………………………………… | $ 70.00 |

Note: All rates above are for regular business hours and do not include travel time. Overtime rates are x 1.5 and any disbursement costs, unless specifically stated, have not been included and will be charged at the per diem rate or actual cost, whichever is higher plus 15% administration fee. Mileage per diem is $0.55/km for company vehicles, hotel per diem is $150/night per employee, meal allowance per diem is $90/day per employee. Other costs such as printing, and courier costs are charged at cost plus 15% administration fee.

SCHEDULE B:

STANDARD TERMS AND CONDITIONS, revised January 1st, 2025

Schedule A and Schedule B form an integral part of the Mann proposal (“Proposal”). The Proposal containing the proposed "Scope of Work", together with Schedule A and Schedule B, are collectively referred to as the "Agreement".

Article 1: General

1.1(a) The Agreement, when accepted in writing by the Client and Mann shall constitute the entire, complete and exclusive agreement between the parties relating to the services specified in the Agreement ("Services") and shall supersede and cancel all prior agreements and understandings, written or oral, relating to the subject matter of the Agreement. The Agreement and any rights or obligations there under may not be assigned by either party without the advance written consent of the other, with the exception that Mann may assign all or part of the Services to the related construction company, Aris Building Technologies (“Aris”) at any time without notice to the Client.

- The terms and conditions of this Agreement shall not be modified or rescinded except in writing, signed by a corporate officer of Mann. Mann's performance under this Agreement is expressly conditioned on Client's assenting to all of the terms of this Agreement, notwithstanding any different or additional terms contained in any writing at any time submitted or to be submitted to Mann by the Client.

- The terms and conditions set forth herein shall supersede, govern and control any conflicting terms of the Proposal.

  - If, during or within 90 days after the term of this Agreement, Client engages any Mann employee who has performed work under this or any other agreement between Client and Mann, Client shall pay Mann an amount equal to the employee's latest annual salary.

  - This Agreement shall be governed by and enforced in accordance with the laws of the Province of Ontario.

  - The Services shall be performed during Mann's normal working hours, Monday through Friday inclusive, excluding holidays, unless otherwise set forth herein.

  - Client will at all times designate a contact person with authority to make decisions for Client regarding the Services. Client will provide Mann with information sufficient to contact such person in an emergency. If such representative cannot be reached, any request for Service received from a person located at Client's premises will be deemed authorized by Client, and Mann will, in its discretion, act accordingly.

  - Mann will be permitted to control and/or operate all equipment necessary to perform the Services and will be allowed to perform routine research and development on Client equipment at the expense of Mann.

  - Mann will not be required to conduct safety or other tests, install new devices or equipment or make modifications to any equipment beyond the Proposal set forth in this Agreement. Any Client request to change the Proposal or the nature of the Services must be in the form of a mutually agreed change order, effective only when executed by all parties hereto.

  - Client agrees that any carbon credits associated with this work will be the ownership of Mann unless agreed otherwise in writing.

  - Client agrees that Mann’s obligations, liability and warranty under the Agreement are limited by the obligation of Mann to design and control the Clients buildings in order to provide the minimum required temperature, air flow and other parameters that may be specified by the Ontario Building Code (“OBC”) or other applicable governing municipal, provincial or federal requirements. In the lack of such requirements, then the Mann design shall be deemed to be accepted by the Client. Any request by the client or his site staff to increase the temperature or other parameter above that specified by Mann or the OBC shall constitute a waiver by the Client of any performance guarantee offered by Mann in the Agreement.

  - In the event that the Client terminates this Agreement for any reason whatsoever but at a time when more than 50% of the Services are (a) completed by Mann or (b) invoiced by Mann, then the Client will be liable to pay the entire fee specified for the Services only conditional that Mann invoice the balance of the Services.

  - Mann has the right to modify any Mann design, drawing or specification at any time if Mann, in its exclusive capacity, determines that there is a defect that will impact the performance of the Services.

Article 2: Charges, Fees and Invoices

  - Payments to be made under this Agreement will provide for, and be in consideration of, only Services specifically included under the Proposal. All other Services, including but not limited to the following, shall be separately billed or surcharged on a time and materials basis: (a) emergency services performed at Client's request, if inspection does not reveal any deficiency covered by this Agreement; (b) services performed other than during Mann's normal working hours; and (c) service performed on Equipment not covered by this Agreement.

  - Invoices are due upon receipt or otherwise as may be set forth therein. If any payment is not received when due, Mann may deem Client to be in breach hereof and may enforce any remedies available to it hereunder or at law, including without limitation suspension or termination of Services and acceleration of payments, including any payments specified under 1.10. Any amount not paid within thirty (30) days of the date due shall accrue interest from the date due, until paid, at the rate of twenty-eight percent (28%) per annum. In the event of a dispute by Client regarding any portion or all of an invoiced amount, the undisputed portion shall be paid when due, and interest on the disputed, unpaid portion shall accrue as aforesaid, from the date due until the date of payment, to the extent that such amounts are finally determined to be payable to Mann.

  - Client is responsible for paying any present or future sales, use, occupancy, goods and services, excise or other federal, provincial, or local tax due or owing as a result of this Agreement.

  - All extra work for the Proposal shall be billed using the rates listed in Schedule B

  - All mileage is charged from Mann office located at 150 Bridgeland Ave. Any Services that are performed more than 50km from the local Mann office will be rounded up to a full day’s labour.

  - A minimum of 4 hours per worker may be charged for mobilization, prior to start of the Services.

  - Any change to any Mann design, drawing, or specification after the tender or after award of purchase order, whichever comes first and regardless of the reason for the change is subject to additional fees as per the Standard Billable Rates.

  - The initial Mann design will be revised one time based on Client comments. Further revisions will be charged per the Standard Billable Rates.

Article 3: Allocation of Risk

  - Mann provides a one year warranty for errors or omissions from the Services, unless specified otherwise.

  - THE EXPRESS LIMITED WARRANTIES PROVIDED ABOVE ARE IN LIEU OF AND EXCLUDE ALL OTHER WARRANTIES, STATUTORY, EXPRESS, OR IMPLIED, INCLUDING WITHOUT LIMITATION ANY WARRANTY OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE, WHICH ARE HEREBY EXPRESSLY DISCLAIMED. Mann MAKES NO WARRANTY, EXPRESS OR IMPLIED, THAT ANY EQUIPMENT PROVIDED HEREUNDER WILL PREVENT ANY LOSS, OR WILL IN ALL CASES PROVIDE THE PROTECTION FOR WHICH IT IS INSTALLED OR INTENDED. THE LIMITED EXPRESS WARRANTIES AND REPRESENTATIONS SET FORTH IN THIS AGREEMENT MAY ONLY BE MODIFIED OR SUPPLEMENTED IN A WRITING SIGNED BY A DULY AUTHORIZED CORPORATE OFFICER OF Mann.

  - Mann will indemnify Client from and against losses, claims, expenses and damages (not including legal fees and expenses on both a solicitor and client basis) for personal injury or physical damage to property, but not loss of use of the property resulting from such damage or from damage to any work performed hereunder. Such indemnification shall be solely to the extent caused by or arising directly from Mann's or its employees', consultants' or agents' negligent acts or omissions or willful misconduct in connection with its performance of Services hereunder. Mann's obligations under this indemnity provision shall not extend to claims, losses, expenses and damages arising out of or in any way attributable to the negligence of Client or its agents, consultants or employees other than Mann. Mann's liability to Client or any third party under this Section or otherwise under the Agreement is expressly limited to, and Mann shall not be liable other than for the direct losses, claims, expenses and damages arising as aforesaid. Mann shall in no event be responsible under this Agreement for incidental, consequential, punitive, exemplary or special damages, including without limitation lost profits and/or lost business opportunities, whether arising in warranty, late or non-delivery of any Equipment or Services, tort, contract or strict liability, and regardless of whether Mann has been advised of the possibility of such damages. Mann reserves the right to control the defense and settlement of any claim for which Mann has an obligation to indemnify hereunder. The parties acknowledge that the price for which Mann has agreed to perform its Services and obligations under this Agreement has been calculated based upon the foregoing limitations of liability, and that Mann has expressly relied on, and would not have entered into this Agreement but for, such limitations of liability.

Article 4: Environmental

  - Except as disclosed, Client represents that there is no asbestos or any other hazardous or toxic materials, as defined in any applicable federal, provincial or local law, ordinance, rule, code or regulation relating to public health or safety or protection of the environment ("Hazardous Materials"), present at Client's locations where Services are performed. Mann will notify Client immediately if it discovers or suspects the presence of any Hazardous Material. All Services have been priced and agreed to by Mann in reliance on Client's representations as set forth in this Section 4.1 The presence of Hazardous Materials constitutes a change in the Proposal equivalent to a change order whose terms must be agreed to by Mann before its obligations hereunder will continue.

  - Client shall be solely responsible for testing, abating, encapsulating, removing, remedying or neutralizing such Hazardous Materials, and for the costs thereof. Even if an appropriate change order has been entered into pursuant to Section 4.1 above, Mann will continue to have the right to stop providing Services until the job site is free from Hazardous Materials. In such event, Mann will receive an equitable extension of time to complete its Services, and compensation for delays caused by Hazardous Materials remediation.

  - Client warrants that, prior to the execution of the Agreement, it has notified Mann in writing of any and all Hazardous Materials present, potentially present or likely to become present at Client's locations and has provided a copy of any jobsite safety policies, including but not limited to lock-out and tag procedures, laboratory procedures, chemical hygiene plan, material safety data sheets, and other items covered or required to be disclosed or maintained by federal, provincial, or local laws, regulations or ordinances.

  - Client hereby indemnifies and holds harmless Mann from and against any damages, losses, costs, liabilities or expenses arising from Client's breach of, or failure to perform its obligations under, Sections 4.1, 4.2 or 4.3 above.

Article 5: Client Responsibilities

  - Client will operate and maintain all building, HVAC or process equipment (“Equipment”) in accordance with applicable manufacturer's specifications, including those set forth in the manufacturer's operating manuals or instructions, as well as all requirements of applicable law or of authorities having jurisdiction. Such Equipment shall be operated only in the specified operating environment, which shall be supplied by Client, including without limitation: (a) suitable electrical service, including clean, stable, properly conditioned power, to all Equipment; (b) data lines, capacity and connectivity as required by such Equipment; and (c) heat, light, air conditioning or other environmental controls, and other utilities in accordance with the specifications for the Equipment. Failure to so operate the Equipment will allow Mann the exclusive right to terminate immediately any Service obligations Mann may have hereunder.

  - Client will promptly notify Mann of any unusual operating conditions, system malfunctions or building changes that may affect the Equipment or any Services.

  - Client will provide Mann with reasonable means of access to the Equipment and shall make any necessary provisions to reach the Equipment and peripheral devices. Client will be solely responsible for any removal, replacement or refinishing of the building structure or finishes that may be required to gain access to such Equipment.

  - Client shall properly dispose of all ballasts, mercury bulb thermostats, used oil, contaminated filters, contaminated absorbents, refrigerant and any other Hazardous Materials that at any time are present at Client's premises, in accordance with all applicable federal, provincial, and local laws, regulations, and ordinances. At no time and under no circumstances will Mann be responsible for any such removal or disposal and Client hereby indemnifies and holds Mann harmless from and against any liability or claim arising there from.

  - Client will, if applicable, provide and pay for an internet connection with static IP address in a mutually agreed upon location. All web based service Equipment will remain the property of Mann unless otherwise stated herein.

  - Client will allow Mann to provide scientific research, experimentation and development (SRED) on software or hardware installed by Mann in order to increase the efficiency or performance or any other technical improvement that may be identified by Mann. All costs of the SRED work including labor and materials shall be at the cost of Mann. To perform SRED, Mann reserves the right to change equipment or add monitoring equipment at no cost to the Client.